## Slide 1: SOLEIL II : an almost complete dismantling scenario
François TRIAS on behalf of SOLEIL II Project team
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 2
The dismantling & disassembling scenario
Challenges and constraints
Traffic on site
Dismantling strategy (full Radiation Safety measurements)
Crane strategy: the sinews of war
Flying over working areas with safety (tunnel & exp hall)
Slabs handling management
Dismantling method (straight sections then arcs)
Dismantling planning
Summary :
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 3
Challenges and constraints
Dismantling of SR to be carried out as quickly as possible: work in 2 shifts in 2 different areas => 4 teams of authorized crane workers required/5 days a week
Handling with two cranes at the same time => coactivity management, evacuation on 5 unloading zones to streamline handling
Minimum 2 closed cells between 2 open cells
Obligation to process straight sections before arcs
No workers in adjacent closed cells during slabs handling
Handling heavy loads on slabs with specific protocol : safety reason
Evacuation of specific beamlines hutch when flown over by cranes
Permanent rotation of evacuations from the unloading areas to the disassembly building with forklift, trailers, etc.
Safe circulation on site with other users
  Critical path planning
  Just-in-time logistics
  Resources available
  Maximum safety
& the same items and timing with the booster equipments & 7 beamlines full Upgrade (location change) !!!
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 4: Road Traffic on Site – Removal SR & Booster during Shutdown
Evaluation of the number of journeys with forklifts, trailers, to the different buildings: RS, Temporary storages, storages and modifications
To be completed by Beamlines movements.
Most will take place inside Synchrotron building
T5
T2
T3
T4
T1
Traffic flow assumptions
RS
Temporary building #2 :
1900 m2
- Radiation Safety : dismantling, measurements, storages
Temporary building #1 :
- New machine equipments storages
- BL2 storages
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 5: Dismantling strategy - full Radiation Safety control by requirements of ASN (Autorité de Sûreté Nucléaire /Nuclear Safety Authority) : a project IN the Upgrade project
The absolute rule : any equipment or accessory leaving the tunnels must be measured in RS
Estimated weight of tunnels equipment :
More than 650 tons (including cooling system) of various materials from SR
More than 150 tons of various materials from Booster
 | TOTAL SR
Weight (t) | 600,4
Steel | 495,1
Stainless Steel | 12,9
Al | 34,4
Copper | 36,2
Plexi | 0,6
Needs : procedures, methods, safety rules, available resources, logistics are necessary to succeed in this challenge !!
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 6
Dismounting steps of a sextupôle magnet
The related BOM (Bill Of Material) specify the material of each component.
Disassembly down to the unique screw for the RS measurements.
3 hours are needed for 1 person to completely disassemble a sextupole magnet.
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 7: Disassembly at RS : a new building
Useful area : ~1700 m2 - Covered area to site exit : 105 m2
Zone stockage av et après mesures 150 m2
Zone stockage av et après mesures 150 m2
Project
Storage & Disassembly area
RS measures area
Recycling area 3
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 8: SR removal : Cranes strategy, the sinews of war
NW loading/unloading zone
NE loading/unloading zone
Passerelle N
Passerelle E
Study of the pathways is almost complete.
We foresee to bring the larger and heavier equipment directly toward the two loading/unloading zones (named SAS, Synchrotron exits)
To shorten the crane time using and to facilitate the simultaneous use of the two cranes at the opposite sides of the ring, the girders will be moved passing above the passerelle E (bridges).
It will not be possible for the insertion devices because the available height over the bridge is not sufficient. Then we foresee to move them under the bridges thanks to motorized skates.
For the other equipment we foresee to have temporary storage areas close to the outer circulation area of the experimental hall (named passage way) and evacuate them with pallet truck or forklift.
C01
C02
C03
C04
C05
C06
C07
C08
C09
C10
C11
C12
C13
C14
C15
C16
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 9: Uninstallation – Cranes fly over areas
Fly over corridor between tunnel & loading/unoading areas
Sextants
Antares
Tempo
West SAS
East SAS
Loading & unloading areas
SR fly over areas, SR exit doors & handling areas
During the dismantling study, we found that the use of both cranes is the most important constraint :
The SD planning critical path is determined by the permanent use of cranes, their speed transport, number of equipment to be handled and the safety rules.
The slabs handling has been a specific focused point
A special cranes maintenance plan will be implemented before & during the shutdown to secure the cranes activity
Crane area 1
Crane area 2
Crane separation line
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 10: Circulation area for girders & ID’s above slabs
T3
Bat Infra
0,2 m
1 meter
around 40 cm
Visual device like string
clearance between slabs
Upper slab
Lower slab
Inside tunnel
Necessary conditions to allow inside tunnel work with circulations above slabs : OK safety group
In case of accidental fall, the lower slab will not be damaged => no risk of injury for working people inside the tunnel
- 20 cm above slabs
- 1 meter from railing
- visual device installed
Handling areas | Beam lines to be evacuated when cranes flying over |  | 
WEST LOADING ZONE | SMIS | AILES | 
EAST LOADING ZONE | DEIMOS * | CRISTAL | PUMA
TEMPO Temporary loading zone | SAMBA | (Futur DESIRS) | 
ANTARES Temporary loading zone | ANTARES | ROCK | 
SEXTANTS Temporary loading zone | SEXTANTS | SIXS | 
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 11: Remove – Focus on slabs handling
925 slabs to be handled twice (Remove/Installation), some of them several times (about 100)
=> Important safety & planning challenge
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 12: Remove - Focus on timing evacuation & organization
Time table for evacuation of equipment for the complete Storage Ring
Crane 1 |  |  |  | Crane 2 |  |  | 
Cell | Opened slabs Nber | Time in h | Total time | Cell | Opened slabs nber | Time in h | Total time
SDM 14 | 22 | 10,3 | 10,3 | SDM 06 | 17 | 7,9 | 7,9
SDM 15 | 21 | 9,8 | 20,1 | SDM 07 | 19 | 8,9 | 16,8
SDM 16 | 21 | 9,8 | 29,9 | SDM 08 | 19 | 8,9 | 25,7
SDL 01 | 46 | 21,5 | 51,3 | SDM 10 | 21 | 9,8 | 35,5
SDM 02 | 20 | 9,3 | 60,7 | SDM 11 | 21 | 9,8 | 45,3
SDM 03 | 26 | 12,1 | 72,8 | SDM 12 | 21 | 9,8 | 55,1
SDM 04 | 21 | 9,8 | 82,6 | SDL 13 | 29 | 13,5 | 68,6
SDL 05 | 29 | 13,5 | 96,1 | ARC 13 | 42 | 19,6 | 88,2
ARC 14 | 44 | 20,5 | 243,6 | ARC 12 | 39 | 18,2 | 106,4
ARC 15 | 44 | 20,5 | 223,1 | ARC 07 | 44 | 20,5 | 213,7
ARC 16 | 38 | 17,7 | 202,5 | ARC 06 | 49 | 22,9 | 236,6
ARC 01 | 55 | 25,7 | 184,8 | ARC 05 | 27 | 12,6 | 249,2
ARC 02 | 50 | 23,3 | 159,1 | ARC 11 | 46 | 21,5 | 127,9
ARC 03 | 48 | 22,4 | 135,8 | ARC 10 | 46 | 21,5 | 149,3
ARC 04 | 37 | 17,3 | 113,4 | ARC 09 + SDL 09 | 55 | 25,7 | 175,0
 |  |  |  | ARC 08 | 39 | 18,2 | 193,2
TOTAUX | 522 |  | 243,6 |  | 534 |  | 249,2
 |  | Shifts nber | 34,8 |  |  | Shifts nber | 35,6
Estimated meantime for handling a slab : 10 to 14 minutes each.
5 hours for 22 slabs
216 hours or
31 shifts for all slabs
With all logistics tools & staff as :
Chain slings (with spares)
Wooden blocks
Safety equipment
Area marking equipment
Free areas & paths to evacuate to RS building
Forklift & trailers
Plans & procedures
Authorized staff
Special safety staff
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 13: Dismantling - Equipment Evacuation Sequencing with O/C Slabs
Closed Tunnel
SS & FE Evacuation :
about 10 h
Opening 22 slabs :
about 5h
Closing 22 slabs :
about 5 h
Total time: opening, evacuation, closing :
about 20 hours or 3 shifts or 1.5 days
Specific defined area for slabs storage on both sides of aperture
Example for SS 14 : include 2 ID’S & 1 front end
We are used to open/close slabs at every periodic shutdown
« We do what we are familiar with »
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 14
11 slabs
SS 14
Expansion : + 10 % of occuped area
Expansion : + 10 % of occuped area
Dismantling – slabs removal SS 14 – Top view animation
11 slabs
C 13
C 14
C 15
C 14
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 15
Equipement removal SS14 – Simulation
C 13
C 14
C 15
C 14
PAU WS - Removal & Installation 18-20 March 2024 - Trieste
Opened straight section 14

## Slide 16
11 slabs
SS 14
Slabs re installation (closing SS14) – Simulation
11 slabs
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 17: Dismantling – equipment evacuation areas when closed tunnel
WEST SAS
EAST SAS
Sextants
Antares
Tempo
AS1
AS 2
AS 3
AS 4
Achromats
Straight sections
Crane area 1
Crane area 2
South tunnel exit
East tunnel exit
North tunnel exit
West tunnel exit
Safety screen gate
Tunnel exit
Evacuation handling area by crane
For :
- Recovered equipments
- Cables, cable trays
- Piping
- Waste in crates
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 18: Dismantling – tunnel areas to be evacuated & passageway used
WEST SAS
EAST SAS
Sextants
Antares
Tempo
Antatomix/ nanoscopium : crossing passageway beamlines
GOAL : minimize time crane handling
Crane separation line
Handling with crane
Handling with forklift by passage way
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 19: Dismantling – straight sections & arcs management
WEST SAS
EAST SAS
Sextants
Antares
Tempo
AS1
AS 2
AS 3
AS 4
SS & Arcs: Optimized management to release AS 1 area at first
End AS1
EndAS 3
End AS 2
EndAS 4
Achromats
Straight sections
12 slabs to be evacuated by West SAS at SS02 & 03 => time to be added
Zone pont 1
Zone pont 2
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 20: Dismantling machines – Estimated schedule
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 21: Following works, & installation studies
To be completed :
More detailed works in technical zone removal
Strategy for non machines network as cooling system, safety system, communication system inside tunnel, etc,…
Civil works and then ….
Working on news machines (SR & booster) installation & BL2 Upgrade program
Your questions are welcome !!!
Our daily/weekly life !!!
Thank you very much for listening !!
PAU WS - Removal & Installation 18-20 March 2024 - Trieste

## Slide 22: Optional slide : Buildings allocation
Temporary building #1 :
2x1500 m2 => 3000 m2
- New machine equipments storages
- BL2 storages
East ear : 250 m2
- Vacuum strings construction
Center of the Booster : 1500 m2
- Activated equipments storages
- New power supplies equipments
- Other storages
West ear : 250 m2
- BL2 Storages & Labs to be confirmed
South ear : 250 m2
- BL2 storages to be confirmed
Experimental hall :
- Tempo area (450 m2) : Mock Up, strings vacuum storage, Id’s upgrade
- Inside passageway (150 m2)
- Internal technical area BL2 (380 m2)
Workers accomodation
500 m2
Temporary building #2 :
1900 m2
- RS : dismantling, measurements, storages
Recycling area 1
T5 : 430 m2
- Magnets & girders assembly & measurement
- ID’s construction
T1 : 400 m2
- Front end vacuum construction
- Various storage
T2 & T3: 460 m2
- Various Storage whose Matching assembly girders
T4 : 230 m2
Magnets lab
ID’s construction
Booster & LINAC roof : 200 m2
- Power supplies construction
RP
Recycling area 3
Recycling area 2
T5
T2
T3
T4
T1
T1
Estimated areas (Existing, transformed, temporary) - m2 | 10 900 | on site | 9 900
 |  | off site | 1 000
Estimated area requirements - m2 | > 10 500 | Machine | 5 000
 |  | Beam lines | 3 500
 |  | RS | 1 500
 |  | Workers | 500
 |  | Cooling Cables Control Booster | ?
PAU WS - Removal & Installation 18-20 March 2024 - Trieste