## Slide 1
ESRF-EBS TECHNICAL ZONE PREPARATION
&
CABLING
3rd Workshop on Particle Accelerator Upgrade
Removal and Installation (PAU-R&I3)
Trieste, 17-20 March 2024
Benoit Joly
Old ESRF Storage Ring
ESRF-EBS

## Slide 2: contents
Technical Zone preparation
Description & planning New layout for the electronic cubicles Improvements made to the electronic cubicles
Cabling A milestone task Activities and contracts Planning and progress Main challenges VDC distribution for the magnet power supply Total figures

## Slide 3: Description of the Technical Zone
“If the storage ring, with its innovative new lattice configuration, is the beating heart of the EBS, then the Technical Zone is the circulatory system of arterial cables and pipes that connects magnets, detectors and myriad other equipment from the storage ring to the brains of the operation – the Control Room”.
Metres of cables and pipes link the hardware in the storage ring to the software in the Control Room. Credit: A. JOLY & C. ARGOUD / ESRF.

## Slide 4: Description of the Technical Zone
SRDC
SRRF 1&2
SRRF 3
InjExt
Technical zones
(More than 500 elec. cubicles)
InjExt Platform
SRDC
3xSRRF
Technical Areas
SY TU
SR TU
LINAC
- Freeway - 32 x Electronic cubicle zones - Storage areas and laboratories - Liquid Nitrogen network
- …
The Storage Ring Tunnel (3 670 m2)
The Technical Zone (5 300 m2)

## Slide 5: ESRF-EBS Planning

## Slide 6: Old electronic cubicle layout

## Slide 7: New electronic cubicle layout
ESCAPE ROUTE
STORAGE AREA
DROP ZONE
HOT SWAP Cubicle
CRYO
SYSTEM

## Slide 8: Electronic cubicle Improvements
Mains distribution via the 230V power sockets Replacement of the ageing power sockets with new power supply sockets fitted to 19” rack.
Improvement of the cable path inside the cubicle Addition of a second cable tray in order not to have all the cables running on one side of the cubicle only.
Computing Network distribution in each cubicle In the same way that the 230V power supply is distributed in each cubicle, Computing Network patch panels have been installed in each cubicle requiring a Network connection.
Low voltage DC distribution in the cubicles 24VDC : reliable and redundant power supply for the instrumentation (made from 230V). 48VDC : the Network switches stay ON in the event of a power failure (specific power supplies with battery).
Better routing of the low current cables Installation of interconnected cable trays above the cubicles.

## Slide 9: OLD cabling organisation
SR Tunnel
Trench
Low level signals
Optic fibers
Network cables
Serial lines
Bottleneck!
One row of
cubicles only…
TZ

## Slide 12: new cabling organisation
SR Tunnel
Trench
Optic fibers
Network cables
Serial lines
Low level signals
Cable trays above the cubicles
TZ

## Slide 13: new cabling organisation
SR Tunnel
Trench
Optic fibers
Network cables
Serial lines
Low level signals

## Slide 14: Control & instrumentation HARDWARE
DIAG
NETWORK
POWER
SUPPLY
VACUUM

## Slide 15: new layout organisation
Credit: C. ARGOUD / ESRF.

## Slide 16: Cabling - a milestone task
Remaining connection of SR equipment
Installation of remaining diagnostics & control equipment
Installation of equipment and service outside SR tunnel (+ Remote control configuration)
Cabling in SR
Disconnection of cables
Dismantling old equipment
Reorganisation of cubicles
Preparation of new equipment
Refurbishment of reused equipment
Test of each individual signal
(Supply, monitoring & interlocks)
Test of functionalities
(Local and remote control)
Work after cabling
Work before cabling
Cabling was the link between SR installation, TZ installation and equipment tests

## Slide 17: Cabling - activities
A new cable database was fully updated with the new cubicle layout
It was used for any cabling requests
Magnets
Accelerator engineering
Power supply and electrical engineering
Radio frequency
Control upgrade
Diagnostics
Injector upgrade
Vacuum
Transfert line 2
Main electrical activities
Management of the cable database
New cabling system from the technical zone (TZ)
Supply and installation of the cable trays and the grounding network inside the SRTU
Supply, installation, labelling and test of all the cables with connectors on both sides, i.e. from the electronic cubicles located in the TZ to the various equipment of the new accelerator inside the SRTU
Cable database
Electrical demands

## Slide 18: Cabling - contracts
Electrical cabling in
SRTU / TZ / SRDC
Batch 1: Cabling in the SRTU
Batch 2: Cabling in the SRTU
DC DC Distribution (main)
DC DC SRDC final connections to the grid
CFT 2580 - SPIE
CFT 2580 - ACTEMIUM
CFT 2503 - BONNAZZA
(WP4)
Move of electrical cubicles (baking)
RFQ 2731 - BOUYGUES
48VDC + 24VDC electrical distribution for the computing network
CFT 2723 - INEO
Dismantling of cell 32, 01 & 02
RFQ 2789 - INEO
Dismantling of TL2
RFQ 2790 - BONNAZZA
Dismantling of electrical cubicles
TZ01-08
RFQ2784 - BOUYGUES
Replacement of main electrical switch boards 1MD4-5-6 (WP4)
CFT 2774 - BONNAZZA
Notes: The two main contractors had a different approach for the teams management. Contractor for one and temp agency for the other.
Actemium is a big group that used his national network. Spie was smaller and used local staff (smaller pool of technician).

## Slide 19: Cabling - planning and progress
Three years of preparation for six months of works
ESRF-EBS SHUTDOWN
STUDIES
CFT EXERCICE
CONTRACTS
PREPARATION STUDIES & PROCUREMENT
PREASSEMBLY PHASE
CABLING WORKS
ESRF VALIDATION PROCESS
ADDITIONAL CABLING REQUEST
ADDITIONAL WORKS
AMENDMENT 1
AMENDMENT 3
AMENDMENT 2
The technical specifications were done in September 2017 to launch the Call For Tender process beginning of 2018
End of the cabling specifications writing
Nbr of Cables
10 490
Nbr of Cables
13 930
Nbr of Cables
13 400
Six months
Additional works arose during the dismantling phase and the cabling of the first cell
30% additional cables have been requested throughout the project
Three amendments have been done to update the contract with the increasing number of cables and the additional works (done only for the two main contractors ACTEMIUM and SPIE) Increase of 13% of the initial budget (quite low compared to the volume of works and the uncertainties)
Preassembly phase in the workshop prior to the shutdown to limit the installation time on site
Three months

## Slide 20: Cabling - Main challenges
To do:
32 cells to be wired with the same specifications regarding the installation of the cables, depending on their type and use.
Many of the 32 cells were different; they did not have exactly the same equipment and not exactly the same configuration.
Very short response time in the event of a problem (reaction and adaptation).
e.g. Only two weeks to wire eight cells in parallel (more than 100 electricians at the peak load).
RF cavities, collimators, diagnostic equipment
Proximity of transfer lines, different position and length of cable trenches, different layout of technical areas
How to:
We relied on experienced technicians and manager of the Electrical unit to do a close follow-up of the works
Technicians were assigned to each company, with the mission to:
monitor the progress of the work on a daily basis
deal with small problems and necessary adaptations in the field
point out the main difficulties and report
ensure compliance with initial specifications as well as adaptations decided following a change

## Slide 21: Cabling - Main challenges
To do:
Throughout the project, we received approximately 160 requests for additional cables, adaptations or changes to specifications. How to keep track of these wiring tasks and account for each adjustment ?
How to:
We relied on the use of ticket trackers
Each requester had to send their request via email.
A ticket was created and saved automatically.
Thanks to JIRA ticket trackers, requests could be analysed, sorted and assigned to companies.
Then, the quotes according to the terms of the contract, were returned by the companies and the requests were validated via the ESRF change request process.
Finally, the new requests were included in the wiring workflow and their main steps recorded in the corresponding ticket.

## Slide 22: Cabling - Main challenges

## Slide 23: Installation of the VDC distribution for Power supply
Section 120 mm2
260 cables installed
Total length 24 870 m
Length of cable between 30 to 550 m
Installation done prior to long shutdown, during Machine shutdowns only (~12 weeks)
Credit: S. CANDE
Credit: C. ARGOUD / ESRF.

## Slide 24: Cabling – total figures
3 years of preparation for 6 months of works
60 000 hours of works
220 electricians throughout the project
100 electricians at the peak load
14 000 cables installed
360 km of cables
15 500 connectors
Less than 100 faulty cables
Credit: S. CANDE
Credit: C. ARGOUD / ESRF.

## Slide 25: Many thanks for your attention
Credit: VUEDICI.ORG / ESRF

## Slide 26: Clearing out

## Slide 27: Mark out & sign post

## Slide 28: Drop zone for dismantling
Credit: S. CANDE
Credit: C. ARGOUD / ESRF.
Credit: C. ARGOUD / ESRF.

## Slide 29: Hot Swap Cubicle cabling

## Slide 30: piping
Two main steps.
Pre-manufacturing :
80% of the added value
On site assembly :
20% of the added value